## Slide 3
Chart: Monthly Consumption Cubic Meters with annual totals
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sept | Oct | Nov | Dec
2016: 96427 | 3137 | 3456 | 4077 | 6321 | 13027 | 11835 | 15843 | 16719 | 10105 | 4102 | 3602 | 4203
2017: 120275 | 4203 | 5684 | 5084 | 3620 | 6167 | 17285 | 21335 | 25458 | 17024 | 5768 | 5105 | 3542
2018: 105052 | 3442 | 3490 | 4506 | 4350 | 13892 | 14453 | 19177 | 20798 | 7247 | 4101 | 4547 | 5049
2019: 99772 | 5471 | 3316 | 3622 | 5052 | 11756 | 18738 | 14708 | 16423 | 8321 | 4796 | 4187 | 3382
2020: 93003 | 3955 | 3834 | 3526 | 7863 | 10684 | 10646 | 16284 | 15309 | 8876 | 4781 | 3733 | 3512
2021: 106432 | 3368 | 3242 | 3536 | 7401 | 10684 | 15492 | 24259 | 16105 | 9427 | 4696 | 3893 | 4329
2022: 97697 | 3979 | 4422 | 4707 | 4509 | 5125 | 7786 | 15728 | 19259 | 14828 | 8774 | 3995 | 4585
2023: 97260 | 6098 | 3923 | 3958 | 4156 | 12393 | 17847 | 14318 | 10843 | 9465 | 4996 | 4906 | 4357
2024: ***** | 4280 | 4287

## Slide 4
Chart: Feb 2024 pumphouse Flow LPM x 10

## Slide 5
Chart: Feb 2024 Well levels Mx 10

## Slide 7
Chart: Feb 2024 Pumphouse Chlorine and pH

## Slide 11
Chart: Feb 2024 Pumphouse discharge pressure PSI

## Slide 12
Ships Point Improvement Dist. |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
Well # 4 Draw down test results before and after well redevelopment |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
Jan 2nd 2024 |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
 | Out flow | Discharge | Well 4 |  | Notes |  |  |  |  |  |  |  |  |  | 
Test No. | LPM | PSI | Meters |  |  |  |  |  |  |  |  |  |  |  | 
1 | Static |  | 9.6 | No drawdown as #4 pump not running |  |  |  |  |  |  |  |  |  |  | 
2 | 142 |  | 7.9 | consumer demand |  |  |  |  |  |  |  |  |  |  | 
3 | 287 |  | 6 | Increase outflow/ demand using hydrant at pump house gate |  |  |  |  |  |  |  |  |  |  | 
4 | 376 |  | 4.7 |  |  |  |  |  |  |  |  |  |  |  | 
5 | 500 |  | 2.9 |  |  |  |  |  |  |  |  |  |  |  | 
6 | 595 |  | 1 |  |  |  |  |  |  |  |  |  |  |  | 
7 | 619 |  | < 1 | Low level alarm test stopped |  |  |  |  |  |  |  |  |  |  | 
Conclusion: If we had left it at 500 LPM it would have drawn down to an alarm level I think the stable limit would be closer to 400 LPM |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
30 and 31 Jan 2024 Well #4 Redevelopment performed by Drillwell |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
Feb 1st 2024 |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
 | Out flow | Discharge | Well 4 |  | Notes |  |  |  |  |  |  |  |  |  | 
Test No. | LPM | PSI | Meters |  |  |  |  |  |  |  |  |  |  |  | 
1 | Static |  | 10.1 | No draw down |  |  |  |  |  |  |  |  |  |  | 
2 | 115 |  | 9.2 | consumer demand |  |  |  |  |  |  |  |  |  |  | 
3 | 200 |  | 8.7 | Outflow/Demand increased using Hydrant |  |  |  |  |  |  |  |  |  |  | 
4 | 311 |  | 7.8 |  |  |  |  |  |  |  |  |  |  |  | 
5 | 420 |  | 7.2 |  |  |  |  |  |  |  |  |  |  |  | 
6 | 524 |  | 6.5 |  |  |  |  |  |  |  |  |  |  |  | 
7 | 635 |  | 5.6 |  |  |  |  |  |  |  |  |  |  |  | 
8 | 744 |  | 4.9 |  |  |  |  |  |  |  |  |  |  |  | 
9 | 752 |  | 4.5 |  |  |  |  |  |  |  |  |  |  |  | 
10 | 771 | 44 PSI | 4.4 | Well level is good to 1.0m however we are reaching the top end of the pump capacity hence the low discharge pressure |  |  |  |  |  |  |  |  |  |  | 
11 | 762 | 43 | 3.8 | Normal discharge pressure is between 80 and 90 PSI |  |  |  |  |  |  |  |  |  |  | 
12 | 750 | 70 | 4.5 | Test stopped as low discharge pressure alarm |  |  |  |  |  |  |  |  |  |  | 
13 | Static |  | 10 | No draw down (pump off) static of 10m under 2min (estimated) |  |  |  |  |  |  |  |  |  |  | 
Conclusion: I feel if the pump was capable we could have very easily reached a outflow of 800 LPM with stable well level at above 2m |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
This data matches the data from drillwell, doubling the well capacity after redevelopment |  |  |  |  |  |  |  |  |  |  |  |  |  |  |